Underground Utility Installation – General Notes

1. Caution: City water mains have a typical depth of 36-inches. Actual depths of all Water Utilities Department’s mains such as water, gravity sewer, sewer force main, recycled water, well line, and pure water lines shall be verified by potholing at all crossings with the proposed underground utility line.

2. Water, sewer, recycled water, and pure watermains marked-up hereon are for reference only. Exact locations should be determined from record drawings and field verified.

3. If any proposed underground utility line is within 10 feet of a Water Utilities main per plan or field mark out, then the existing public main must be potholed every 100 ft, or at an interval agreeable to the Water Utilities Inspector, to confirm its location prior to installing the underground utility line. The proposed underground utility line alignment must also be marked out in the field. Depending upon the depth of the underground utility line to the City’s main and installation method, the Water Utilities inspector may make exception to this potholing requirement.

4. Maintain a minimum 5 feet of separation at all times between outside diameter of City mains and the outside dimension of proposed underground utility lines and structures.

5. Contractor shall provide electronic files in AutoCAD compatible or GIS format of the record drawing utility lines prior to the release of bonds.